## Slide 1: Adaptive-ReBIS: Adaptive Renewable-Integrated Energy Management for EV Charging and Appliance Loads
ML day-ahead forecasting | GA and PSO scheduling and sizing | IEEE 33/69-bus validation
Reddy Phaneendra (2300069007) | Peela Sai Vivek (2300069015)
Guide: Dr. G. Swapna | Project Coordinator: Dr. B. Jyothi | Batch 23CRT GET003
Notes: Good morning. Our project is Adaptive-ReBIS: an energy management system that coordinates solar PV, a battery and the grid for an EV charging hub plus building loads such as HVAC and water heaters. It forecasts tomorrow's demand with machine learning, plans the battery with Genetic Algorithm and Particle Swarm Optimisation, and we validate the result on the IEEE 33-bus and 69-bus distribution feeders.

## Slide 2: EV charging and cooling loads stress distribution feeders
217 kW
site peak at 17:00 on 15 May: EV hub + HVAC + lighting together (our load model)
43.9 %
of the site's grid energy falls in the ToD peak hours (06-10, 18-22) when power costs the most
0.883 pu
lowest voltage on the IEEE 33-bus feeder once 5 such sites draw from the grid, below the 0.91 pu (-9 %) limit
EV charging is bursty and lands on the evening peak, exactly when air-conditioning and lighting peak too
Solar is available at noon, demand peaks in the evening: without storage and coordination the mismatch goes to the grid
Fixed rules ("charge on surplus, discharge on deficit") empty the battery before the evening peak arrives
Utilities see higher peak demand, losses and voltage drop; consumers see higher bills and CO2
Notes: The problem. Our site model peaks around 17:00 in May when EV charging, HVAC and evening lighting overlap. A large share of grid energy lands in the ToD peak window. When five such sites sit on the IEEE 33-bus feeder, the tail voltage drops below the Indian -9 percent limit. A simple battery rule doesn't solve it, because the battery is often already empty when the evening peak arrives.

## Slide 3: Objectives
1
Real, localised data
Hourly PVGIS solar/wind/temperature for Hyderabad, TGERC Time-of-Day tariff, CEA grid CO2 factor
2
Forecast tomorrow
Machine-learning model predicts next-day hourly demand of EV + appliance loads
3
Optimise power sharing
GA and PSO decide the hourly PV-battery-grid schedule with adaptive cost / peak / CO2 priorities
4
Optimise sizing
GA and PSO choose PV kWp, battery kWh and wind kW on a full-year simulation
5
Validate on the grid
Load flow on the IEEE 33-bus and 69-bus feeders: voltage, losses, substation peak
6
Report KPIs
Energy cost, peak demand, CO2 emissions and reliability during grid outages
Notes: Six objectives, each maps to one module of the code. Data, forecasting, power-sharing optimisation, sizing, grid validation and the KPIs.

## Slide 4: From the base paper (ReBIS) to Adaptive-ReBIS
Limitation in the base work | What Adaptive-ReBIS adds
Single EV-station application | One EMS for EV hub + HVAC + water heaters + general load behind one meter
Fixed, equal objective weights all day | Hour-dependent (adaptive) weights on cost / peak / CO2 following the ToD windows
Hand-tuned demand, no forecasting | ML day-ahead demand forecast (4 models vs 2 baselines, out-of-sample)
Fixed rule-based dispatch | GA / PSO day-ahead schedule + real-time correction for forecast error
PV / battery sized manually | GA and PSO joint sizing of PV, battery and wind on 8784 hours
Australian tariff and data | Indian data: PVGIS Hyderabad, TGERC ToD tariff, CEA CO2 factor
No network-level check | IEEE 33-bus and 69-bus annual load flow (voltage, losses, peak)
Base paper: A. U. Rehman, J. Lu, B. Du, F. Bai, M. J. Sanjari, "Efficient management of electric vehicle charging stations: balancing user preferences and grid demands with energy storage systems and renewable energy", Applied Energy, vol. 393, 2025, 126147.
Notes: Our starting point is the ReBIS strategy from Rehman et al., Applied Energy 2025. It was one EV station in Australia, with fixed weights and rule-based dispatch. We extend it in seven ways, listed here. The two genuinely new ideas are the adaptive time-varying weights and the forecast-driven optimiser with real-time correction; the rest is thorough engineering: Indian data, joint sizing, and network validation.

## Slide 5: System architecture
Notes: The whole pipeline. One: real data. Two: ML forecast of tomorrow's hourly demand. Three: the day-ahead optimiser, GA or PSO, produces a 24-hour battery schedule using adaptive weights; the exact LP is our check. Four: in real time the controller corrects for forecast error. Five: the site itself, where PV feeds the load first, the battery charges from surplus and discharges by SOC, and the grid covers the rest. Six: we load-flow the result on the IEEE feeders and compute the KPIs. This runs for every day of the year, with the battery state carried from one day to the next.

## Slide 6: Real input data for Hyderabad
Solar, temperature, wind | PVGIS v5.2 (EU JRC), ERA5, 2020, hourly, 8784 h, 17.385 N 78.487 E
Tariff | TGERC FY2023-24 ToD: off-peak Rs 5, normal Rs 6, peak Rs 7 per kWh
Grid CO2 | CEA CO2 Baseline Database: 0.716 kg CO2 per kWh
Distribution feeders | IEEE 33-bus and 69-bus (Baran and Wu), 12.66 kV
Notes: All weather and resource inputs are real: a full year of hourly PVGIS data for Hyderabad. PV yields about 3.7 kWh per kWp per day. Wind is very weak here, a capacity factor of only about 3 percent, which matters for sizing. Tariff is the real TGERC time-of-day structure, CO2 factor from CEA.

## Slide 7: Site load model: EV hub plus appliance loads
EV hub: 8 x 7.4 kW AC + 2 x 30 kW DC chargers; every EV simulated (arrival, energy, charger queue) at 15-min steps
HVAC: driven by the real hourly temperature, occupancy 9-19 h, COP falls as it gets hotter
Water heaters: morning / evening peaks, more in winter
General: lighting, plugs, pumps
Seeded random numbers: every run gives identical results
Notes: We had no metered data for the site, so the load is modelled, but on top of the real temperature series. Each EV is simulated individually with a charger queue. This is the honest point to state: weather and tariff are real, the load is a model.

## Slide 8: ML day-ahead demand forecasting
R2 0.85
Neural network (MLP), vs 0.57 for "same as yesterday"
16.2 %
hourly MAPE, every forecast out-of-sample
16.6 kW
RMSE (persistence 27.8 kW)
Inputs: hour, weekday, season, next-day temperature forecast, load 24 h / 48 h / 168 h earlier, yesterday's mean and peak. Validation: 12-fold month-blocked CV.
Notes: Six forecasters compared. Every forecast is out-of-sample: for each month, the model is trained on the other eleven. The neural network and random forest are clearly better than the naive "same as yesterday" forecast: R-squared 0.85 versus 0.57. EV demand is random by nature, so a perfect forecast is impossible; that is why the real-time layer exists.

## Slide 9: EMS formulation: adaptive multi-objective scheduling
Decision: battery power P_b(t), t = 1..24 h
J = Σ w_c(t)·Cost(t)/C₀ + Σ w_e(t)·CO₂(t)/E₀ + W_p·max φ(t)·P_grid(t) / P₀
Grid(t) = Load(t) − PV(t) − Wind(t) − P_b(t) (import > 0, export < 0, export ≤ 150 kW)
SOC limits 20-95 %, |P_b| ≤ 0.5C, η = 95 %, end-of-day SOC ≥ 50 %
Hours | w cost | w peak | w CO2
ToD peak 06-10, 18-22 | 0.35 | 0.50 | 0.15
Normal 10-18 | 0.50 | 0.20 | 0.30
Off-peak 22-06 | 0.70 | 0.15 | 0.15
Adaptive weights: priority shifts from "cheapest" at night to "lowest grid draw" in the evening peak.
1
Day-ahead plan
End of day D-1: ML forecast of load and PV for day D goes to GA or PSO, which returns 24 battery set-points.
2
Real-time correction
In peak hours the battery absorbs forecast error so grid draw stays at plan. Other hours: unforecast solar surplus is stored, not exported.
3
Peak guard
Every hour, grid import may not exceed the day's planned maximum: the battery charges less or discharges more.
Notes: The heart of the EMS. One decision variable per hour: battery power. The objective is a weighted sum of cost, CO2 and a weighted peak, each normalised by the no-battery case so the weights are comparable. The weights are adaptive: at night cost matters most, in the evening ToD peak the weight moves to grid peak. The schedule must leave the battery at least half full for tomorrow's morning peak. Then three layers: the day-ahead plan, real-time correction, and a peak guard.

## Slide 10: GA and PSO solvers, benchmarked against the exact optimum
1
Genetic Algorithm
Population 150, 500 generations. Tournament selection, blend (BLX-0.3) crossover, Gaussian mutation, elitism. Each schedule repaired to SOC / power limits before scoring.
2
Particle Swarm
100 particles, 500 iterations. Inertia 0.9 to 0.4, c1 = c2 = 1.8, velocity clamp. Same repair and the same objective as GA.
3
Exact LP (benchmark)
The same day-ahead problem written as a Linear Program, solved by HiGHS. Gives the true optimum, so we can measure how close GA and PSO get.
0.45 %
PSO mean gap to optimum over 366 days (95th pct 1.36 %)
1.34 %
GA mean gap to optimum (95th pct 2.35 %)
273 ms
PSO solve time per day (GA 354 ms, LP 3 ms)
Notes: Both metaheuristics are implemented in NumPy and vectorised over the whole population, so a day solves in well under a second. The key point: because this problem happens to be linear, we can also solve it exactly by LP, and that tells us how good GA and PSO are. Over all 366 days PSO is on average 0.45 percent from the true optimum and GA 1.34 percent. Why keep GA and PSO if LP exists? Because once you add non-linear battery ageing, discrete charger control or converter efficiency curves, LP no longer applies; GA and PSO do.

## Slide 11: Solution quality over every day of the year
PSO beat GA on 330 of 366 days. Left: gap to the exact LP optimum. Middle: improvement over no battery. Right: convergence on the peak day.
Notes: Distribution of the optimality gap over all 366 days. PSO is lower on average (0.45 vs 1.34 percent) and at the 95th percentile (1.36 vs 2.35); both have a few harder days, the single worst being 4.7 percent for PSO and 3.3 for GA. The convergence plot shows both on the peak day.

## Slide 12: Optimal sizing by GA and PSO
300 kWp
PV (hits the roof/carport limit: PV pays back)
49 kWh
battery at Rs 15,000/kWh
0 kW
wind: Hyderabad wind too weak (CUF ~3 %)
20.3 %
lower total annual cost incl. capital (48.8 vs 61.2 lakh)
Notes: GA and PSO search PV, battery and wind sizes; each candidate is simulated over all 8784 hours, scored on annualised capital cost plus O and M, energy bill, demand charges, battery wear and a carbon cost. Both converge to the same answer: 300 kWp PV, 49 kWh battery and no wind. Honest finding: at today's battery price the battery barely pays on the bill alone; the right chart shows the optimum battery growing as battery prices fall.

## Slide 13: How Adaptive-ReBIS shares power on the peak day
Solar feeds the load first; surplus charges the battery at noon
Rule-based ReBIS spends its battery in the afternoon and is empty when the evening EV + lighting peak arrives
Adaptive-ReBIS holds charge for the 18-22 h ToD peak, guided by the forecast
Battery is refilled overnight at the off-peak tariff for the next morning peak
Notes: This is one day, 15 May, the highest-demand day. Top: where the power comes from each hour. Middle: battery state of charge, rule-based in orange versus ours in blue. The rule-based battery is emptied in the afternoon; ours waits for the evening peak. Bottom: grid import; our peak is the lowest of the three.

## Slide 14: Full-year results: Design A (economic optimum)
42.2 %
lower operating cost vs grid only (rule-based 41.4 %)
14.5 %
lower annual peak (rule-based 7.9 %)
121 kW
average daily peak (rule 134, grid only 145)
44.5 %
less CO2 (rule-based 45.3 %)
Notes: Every day of 2020, seven strategies. Adaptive-ReBIS with PSO saves 42.2 percent of operating cost versus grid only, slightly more than the rule-based ReBIS, while cutting the annual peak by 14.5 percent versus 7.9 percent. PSO lands on top of the exact LP on forecast. The perfect-foresight LP is an upper bound that needs tomorrow known exactly; the gap to it is the cost of forecast error. Honest note: CO2 is marginally higher than the rule-based scheme, because keeping charge for the peak means a little more battery loss.

## Slide 15: Full-year results: Design B (200 kWh grid-support battery)
43.1 %
lower operating cost vs grid only (rule-based 41.4 %)
13.0 %
lower annual peak (rule-based 9.7 %)
103 kW
average daily peak (rule 130, grid only 145)
48.3 %
less CO2 (rule-based 50.3 %)
Notes: Same comparison with a larger, 200 kWh battery sized for grid support rather than for the bill. With more storage the adaptive scheduler's advantage in peak reduction grows clearly: average daily peak 103 kW with PSO and 98 kW with GA, versus 130 kW for the rule-based scheme. Note that over the real year GA and PSO end within about one percent on cost; GA even gave the lower peak here. Once the plan is near-optimal, forecast quality matters more than the choice of optimiser. CO2: the rule-based scheme is lower (50.3 versus 48.3 percent reduction), because it never charges from the grid; that is the price of holding charge for the peak.

## Slide 16: Battery size: where the adaptive EMS earns its keep
At every battery size the adaptive EMS gives a lower daily peak than the rule (200 kWh: 104 vs 130 kW)
The rule-based scheme barely uses extra capacity for peak shaving; the forecast-driven plan does
Trade-off: the adaptive plan cycles the battery more, so CO2 and wear are slightly higher; the weights are tunable
Notes: This sweep shows the value of the adaptive EMS grows with battery size. A bigger battery with the old rule gives almost no extra peak reduction. Our planner turns capacity into peak shaving. We are open about the trade-off: more cycling means slightly more losses and wear.

## Slide 17: IEEE 33-bus and 69-bus: load-flow model first validated
Base case | Published | pandapower (NR) | Our BFS solver
33-bus real power loss (kW) | 202.67 | 202.68 | 202.68
33-bus minimum voltage (pu) | 0.913 | 0.913 | 0.913 @ bus 18
69-bus real power loss (kW) | 224.95 | 224.96 | 224.96
69-bus minimum voltage (pu) | 0.909 | 0.909 | 0.909 @ bus 65
Two independent solvers: pandapower (Newton-Raphson, open-source) and our own backward/forward sweep
Hour-by-hour cross-check with the sites connected: max voltage difference 2.0e-8 pu
Our BFS is vectorised over all 8784 hours, so a full year of load flow takes about one second
5 identical Adaptive-ReBIS sites at the feeder tails: 33-bus 18, 22, 25, 30, 33 | 69-bus 27, 35, 46, 50, 65
Existing feeder load follows a daily shape peaking at 20:00 (the published bus load = 1.0)
Notes: Before trusting any network result we reproduce the published base cases: 202.67 kW loss and 0.9131 pu on the 33-bus, 224.95 kW and 0.9092 pu on the 69-bus. Both our solvers match. Our own backward-forward sweep agrees with pandapower to better than a millionth of a pu, and since it is vectorised we can run the whole year, not just a few snapshots.

## Slide 18: Feeder impact over the year (Design A)
Case (5 sites) | 33-bus lowest V, pu | 33-bus hours < 0.91 | 33-bus bus-hours < 0.91 | 33-bus losses, MWh/yr | 69-bus lowest V, pu | 69-bus hours < 0.91 | 69-bus bus-hours < 0.91
Base feeder, no sites | 0.913 | 0 | 0 | 983 | 0.909 | 732 | 1464
Grid only | 0.883 | 1704 | 11730 | 1295 | 0.895 | 1239 | 5329
Rule-based ReBIS | 0.883 | 1503 | 10702 | 1148 | 0.895 | 1181 | 5210
Adaptive-ReBIS (PSO) | 0.885 | 1584 | 10649 | 1148 | 0.896 | 1237 | 5235
Notes: Network results for the economic design, five sites on each feeder, every hour of the year. Adding the sites on grid supply alone pushes the 33-bus tail to 0.883 pu, below the 0.91 limit for 1704 hours. PV and the battery schemes reduce both the hours and the losses. With only a 49 kWh battery the battery schemes are close to each other; the next slide shows the 200 kWh design.

## Slide 19: Feeder impact over the year (Design B)
Case (5 sites) | 33-bus lowest V, pu | 33-bus hours < 0.91 | 33-bus bus-hours < 0.91 | 33-bus losses, MWh/yr | 69-bus lowest V, pu | 69-bus hours < 0.91 | 69-bus bus-hours < 0.91
Base feeder, no sites | 0.913 | 0 | 0 | 983 | 0.909 | 732 | 1464
Grid only | 0.883 | 1704 | 11730 | 1295 | 0.895 | 1239 | 5329
Rule-based ReBIS | 0.883 | 1322 | 9782 | 1145 | 0.895 | 1107 | 4885
Adaptive-ReBIS (PSO) | 0.886 | 1558 | 9078 | 1142 | 0.896 | 1200 | 4555
Notes: With the 200 kWh battery. Adaptive-ReBIS gives the best lowest voltage, the fewest under-voltage bus-hours (9078 versus 9782 rule-based on 33-bus), and the lowest losses and substation peak. One honest finding: the rule-based scheme has fewer HOURS below the limit (1322 versus 1558). The reason is that our EMS follows the TGERC tariff, whose peak windows are 6 to 10 and 18 to 22, while this feeder is most stressed from 17 to 21. So part of the battery is spent on the morning tariff peak when the feeder is not stressed. The tariff signal and the network signal do not line up. That is our main future-work item: feed a DSO network-stress signal into the weights.

## Slide 20: Lowest feeder voltage across the year
Duration curve: hours of the year sorted from the lowest voltage up; the left edge is the worst hours
Reliability (Monte-Carlo, 200 years of random outages, about 48 per year): Adaptive-ReBIS serves 70 % of outage-time demand with the 200 kWh battery (rule-based 50 %; 51 % with 49 kWh), because it keeps charge in reserve. Grid-tied PV without a battery serves 0 % (anti-islanding)
Notes: The duration curve shows the whole year at once. And a reliability view: during random grid outages, a site with PV and a battery behind a hybrid inverter can keep serving load; a grid-tied PV system without battery must shut down. These outage statistics are an assumption, stated in the code.

## Slide 21: Implementation and live demo
1
Python + NumPy
2
scikit-learn
3
SciPy HiGHS
4
pandapower + own BFS
5
Streamlit + Plotly
Simulation core, GA and PSO written from scratch, population-vectorised
Ridge, Random Forest, Gradient Boosting, Neural Network forecasters
Exact LP benchmark of the scheduling problem
IEEE 33/69-bus Newton-Raphson and backward/forward sweep load flow
Live dashboard: pick a day, PV / battery size, optimiser; EMS and feeder run live
Live demo
RUN_DASHBOARD.bat (or py -m streamlit run dashboard/app.py)
1. 15 May, PSO: grid peak vs rule-based and grid only
2. Switch optimiser PSO / GA / LP: same answer, different speed
3. Priority slider: lowest bill vs lowest grid peak
4. IEEE feeder tab: tail voltage at 18:00 vs the 0.91 pu limit
5. Forecast tab: ML vs persistence for that week
py run_all.py regenerates every number in this deck
Notes: Everything is open-source Python, and one command regenerates every number in this deck. For the demo, open the dashboard and walk through the five steps on the right.

## Slide 22: Conclusions and next steps
Forecast-driven GA / PSO scheduling beats the rule-based ReBIS on cost and peak at every battery size; PSO is within 0.45 % of the exact optimum on average
Economic design for Hyderabad: 300 kWp PV + 49 kWh battery, no wind; 42.2 % lower operating cost and 44.5 % less CO2 than grid only
On IEEE 33/69-bus feeders the adaptive scheme gives the shallowest voltage dips, fewest under-voltage bus-hours, lowest losses and substation peak; the ToD tariff windows do not match the feeder's stress hours, so a network signal is the next step
Honest limits: modelled (not metered) site load, assumed capital / outage data, flat CO2 factor
Next steps
Smart EV charging (shift / slow sessions) as a second control variable
Battery ageing model in the objective (where GA / PSO beat LP)
Real metered campus / EV-station data to retrain the forecaster
Network-aware weights from a DSO feeder-stress signal (tariff peak 06-10 h is not the feeder peak 17-21 h)
Hourly marginal CO2 factor instead of a flat average
Conference paper write-up
Notes: To conclude: the adaptive, forecast-driven scheduler outperforms the rule-based ReBIS on cost and peak, PSO reaches the exact optimum within a fraction of a percent, the sizing gives a clear economic design, and the network study shows the benefit at feeder level. Next steps: add smart EV charging, a battery ageing model, real metered data and a marginal emission factor.

## Slide 23: References
[1] M. M. Asiri et al., "Short-Term Load Forecasting in Smart Grids Using Hybrid Deep Learning," IEEE Access, vol. 12, pp. 23504-23513, 2024.
[2] W. M. N. Witharama et al., "Advanced Genetic Algorithm for Optimal Microgrid Scheduling Considering Solar and Load Forecasting, Battery Degradation, and Demand Response Dynamics," IEEE Access, vol. 12, pp. 83269-83284, 2024.
[3] A. U. Rehman, J. Lu, B. Du, F. Bai, M. J. Sanjari, "Efficient management of electric vehicle charging stations: balancing user preferences and grid demands with energy storage systems and renewable energy," Applied Energy, vol. 393, 126147, 2025.
[4] M. E. Baran and F. F. Wu, "Network reconfiguration in distribution systems for loss reduction and load balancing," IEEE Trans. Power Delivery, vol. 4, no. 2, pp. 1401-1407, 1989.
[5] M. E. Baran and F. F. Wu, "Optimal sizing of capacitors placed on a radial distribution system," IEEE Trans. Power Delivery, vol. 4, no. 1, pp. 735-743, 1989.
[6] L. Thurner et al., "pandapower - an open-source Python tool for convenient modeling, analysis, and optimization of electric power systems," IEEE Trans. Power Systems, vol. 33, no. 6, pp. 6510-6521, 2018.
[7] European Commission JRC, PVGIS v5.2; TGERC Retail Supply Tariff Order FY2023-24; CEA CO2 Baseline Database for the Indian Power Sector.
Notes: References: the two journal papers from our abstract, the base paper, the IEEE test-feeder sources, pandapower, and the data sources.